## Slide 1: DOE DISCLAIMER
The Views Expressed Are Solely Those Of The Presenters And Not Endorsement By The
U. S. Department Of Energy Is Intended

## Slide 2
Filter Test Facility
Report On The Testing of HEPA
Filters for the DOE
Presented By: Christopher Hart
Protecting People, Products, and Critical Infrastructure
International Society for Nuclear Air Treatment Technologies
35th Nuclear Air Cleaning Conference ● June 3-5 ,2018● Charleston SC
Air Techniques International Test Laboratory

## Slide 3: Air Techniques International Test Laboratory Overview
Air Techniques International Filter Test Laboratory (ATITL) is under contract from DOE to operate the FTF (Filter Test Facility)in Baltimore, Maryland
Secretary of Energy Memo, June 4, 2001, the Filter Test Lab is to be utilized by DOE Site Contractors
Testing service is provided to the DOE complex
DOE work has top priority

## Slide 4: Rejection Categories
Resistance: Criteria of ≤ 1.0 “ w.g. to ≤ 1.3” w.g. depending on minimum rated air flow.
Penetration: ≤0.03% of upstream concentration
Manufacturing Defects:
Filter Frame/Case Defective
Damaged Gaskets
Incorrect Faceguard installation
Incorrect Filter pack installation
Defective media
Sealant problems
Separator issues
Missing rivets or bolts
Not within Dimensional tolerance
Out of square measurements

## Slide 5: Rejection Categories (continued)
P.O/ Specification Discrepancy:
Missing UL labels
Labeled incorrectly***
Filters rated incorrectly***
Wrong model number***
Packaging
Shipping Damage:
(Inspect Damage to Shipping Crates, Pallets & Filter Cartons)
Reject Filter when Damaged

## Slide 6: Summary Of Filter Rejections
** Thru Mar 2018 data not yet finalized
Fiscal Year | Total Tested | Resistance | Penetration | Mfg. Defects | P.O. /Spec. | Shipping Damage | Total Rejected
2009 | 2175 | 1 | 29 | 133 | 52 | 2 | 217
2010 | 4025 | 21 | 25 | 228 | 23 | 2 | 299
2011 | 4636 | 1 | 23 | 477 | 4 | 0 | 505
2012 | 3238 | 0 | 35 | 492 | 67 | 0 | 594
2013 | 3023 | 37 | 42 | 302 | 82 | 5 | 468
2014 | 2525 | 39 | 20 | 199 | 282 | 4 | 544
2015 | 3535 | 5 | 11 | 700 | 380 | 4 | 1100
2016 | 4085 | 0 | 8 | 65 | 297 | 0 | 370
2017 | 2819 | 0 | 12 | 60 | 314 | 1 | 387
2018** | 796 | 0 | 3 | 42 | 3 | 1 | 49

## Slide 7: HEPA FAILURES BY TYPE
Chart: 
Chart: # Failures (Type) by Fiscal Year
Chart: # Failures (Type) by Fiscal Year
| 2009.0 | 2010.0 | 2011.0 | 2012.0 | 2013.0 | 2014.0 | 2015.0 | 2016.0 | 2017.0 | 2018.0
Resistance | 1 | 21 | 1 | 0 | 37 | 39 | 5 | 0 | 0 | 0
Penetration | 29 | 25 | 23 | 35 | 42 | 20 | 11 | 8 | 12 | 3
Manufacturing | 133 | 228 | 477 | 492 | 302 | 199 | 700 | 65 | 60 | 42
PO/Spec Discreps | 52 | 23 | 4 | 67 | 82 | 282 | 380 | 297 | 314 | 3
Shipping Damage | 2 | 2 | 0 | 0 | 5 | 4 | 4 | 0 | 1 | 1

## Slide 8: HEPA FILTER REJECTION BY NUMBER FOR PO/SPEC AND SHIPPING DAMAGE
Chart: # Failures (PO/Specification Discreps & Shipping ) by Fiscal Year
| 2007.0 | 2008.0 | 2009.0 | 2010.0 | 2011.0 | 2012.0 | 2013.0 | 2014.0 | 2015.0 | 2016.0
PO/Spec Discreps | 214 | 55 | 52 | 23 | 4 | 67 | 82 | 282 | 380 | 297
Shipping Damage | 0 | 2 | 2 | 2 | 0 | 0 | 5 | 4 | 4 | 0
Chart: # Failures (PO/Specification Discreps & Shipping ) by Fiscal Year
| 2009.0 | 2010.0 | 2011.0 | 2012.0 | 2013.0 | 2014.0 | 2015.0 | 2016.0 | 2017.0 | 2018.0
PO/Spec Discreps | 52 | 23 | 4 | 67 | 82 | 282 | 380 | 297 | 314 | 3
Shipping Damage | 2 | 2 | 0 | 0 | 5 | 4 | 4 | 0 | 1 | 1

## Slide 9: HEPA FILTER REJECTION BY NUMBER FOR RESISTANTANCE ,PENETRATION AND MANUFACTURING
Chart: Total Filters Rejected by fiscal Year
Chart: # Failures (PO/Specification Discreps & Shipping ) by Fiscal Year
Chart: # Failures (Resistance, Penetration & Manufacturing ) by Fiscal Year
| 2009.0 | 2010.0 | 2011.0 | 2012.0 | 2013.0 | 2014.0 | 2015.0 | 2016.0 | 2017.0 | 2018.0
Resistance | 1 | 21 | 1 | 0 | 37 | 39 | 5 | 0 | 0 | 0
Penetration | 29 | 25 | 23 | 35 | 42 | 20 | 11 | 8 | 12 | 3
Manufacturing | 133 | 228 | 477 | 492 | 302 | 199 | 700 | 65 | 60 | 42

## Slide 10
Filter Testing & Inspection Failures

## Slide 11: Shipped without Crate

## Slide 12: CASE - REJECT

## Slide 13: Fluid Seal - REJECT

## Slide 14: FILTER CRATE DAMAGE

## Slide 15: Loose Gasket - Reject

## Slide 16: Summary
The results from testing & inspecting DOE filter manufacturers have varied during last ten years as shown by the Filter Test Facility (FTF) reports

## Slide 17: Any Questions?
Brian Bolton - Director of ATI Engineering , Operations and Test Lab
Christopher Hart - Lab Manager
Kenneth Rhames - Filter Technician

## Slide 18: DOE DISCLAIMER
The Views Expressed Are Solely Those Of The Presenters And No Endorsement By The
U. S. Department Of Energy Is Intended