## Slide 1
Development of a Low Flow HEPA Filter
for Radiological Applications
Mark T. Sorna, Puget Sound Naval Shipyard
Bremerton, WA USA
Note: The views presented are those of the speaker and do not necessarily represent the views of the DoD, Navy or its components.

## Slide 2: Summary
Intro – Temporary Nuclear Systems
Current State
New Filter Design
Flow Analysis
Review of AG-1, Section FC
Recommendations

## Slide 3: Servicing Nuclear Systems
Temporary Systems
Flexible Radiological Glovebag Containments
Collection Tanks and Bottles
Low flow rates
No current requirements for nuclear filters with rated flow rates below 20 acfm

## Slide 4: Temporary Systems Components

## Slide 5: Filters For Temporary Nuclear Systems
Current State
  Higher Flow Rate – ASME AG-1, Section FK
  Low Flow Rate – Respirator Filters are Common
Glovebags
  American Glovebox Society (AGS) recommends use of 2 cfm respirator filters

## Slide 6: NIOSH Respirator Filters

## Slide 7: NIOSH Respirator Filters
Requirements per 42 CFR 84
The Occupational Safety and Health Administration (OSHA) requires respirators be certified by National Institute for Occupational Safety and Health (NIOSH)
NIOSH test requirements are different than ASME AG-1 Requirements

## Slide 8: NIOSH Respirator Filters
No Rough Handling Test
No Test for Strength and Water Repellency After Gamma Irradiation
Pressure and Velocity Gradients Present in Positive Pressure Applications Not Accounted For in NIOSH Testing
NIOSH Filters Have Custom Attachment Schemes – Complicates Their Use

## Slide 9: New Filter Design
Design Goals:
  Minimize Case Size
  Medium Velocity < 5 ft/min (2.5 cm/s)
  Minimize Velocity and Pressure Gradients
  Case designed to handle operating and test loads
  Design For Easy Attachment
  Minimize Manufacturing Costs

## Slide 10: New Filter Design
Injection Molded
Case and Screen
Nuclear Grade Media
Injection Molded Nut
And Rubber Gasket
Integrated
Baffle

## Slide 11: New Filter Design
Nut Tightened
Finger-Tight
Filter Installed
On Glovebag Wall

## Slide 12: Airflow Analysis Using CFD
Airflow Modeled in ANSYS Fluent
Filter Media Modeled Using Linear Darcy Porous Media Model
  Where:
    ΔP is pressure loss
    μ is viscosity
    v is velocity
    t is the media thickness
    α is the permeability, 1/α is the viscous resistance coefficient

## Slide 13: Results of Analysis

## Slide 14
Chart: Velocity Profile Immediately Upstream Of Filter Medium
Chart: Velocity Profile Through Midpoint Of Filter Medium
Chart: Velocity Profile Immediately Downstream Of Filter Medium

## Slide 15
Chart: Pressure in Media Pack - Filter With No Baffle
Chart: Pressure in Media Pack - Filter With Baffle

## Slide 16
Chart: Pressure Along Axis - Filter With No Baffle
Chart: Pressure Along Axis - Filter With Baffle

## Slide 17: Evaluation of Existing AG-1 Code
Section FK will pertain only to radial filters so Section FC is reviewed
FC-1000 Introduction
  Amendment to scope to cover temporary systems
  Temperatures for temp systems do not generally reach 250 ºF

## Slide 18: Section FC Evaluation
Article FC-3000 Materials
  Material addition for Injection molded material
  Paragraphs FC-3200 & FC-3210 (Special Limitations and Alternate Materials) should apply
Article FC-4000 Design
  Need new paragraph covering non-rectangular filters
  Additional gasket options and faceguard options

## Slide 19: Section FC Evaluation
Article FC-4000 Design (continued)
  Paragraph FC-4200 (Performance Requirements) unchanged
  Paragraph FC-4300 (Seismic) not necessary for temporary system filters
Article FC-5000 Inspection and Testing
  Similar for temporary systems
  Evaluation needs to be done of the existing equipment (Q-76 and Q-107 penetrometers) for suitability to testing at low flow rates.

## Slide 20: Article FC-5000 Evaluation
Rough Handling Test (FC-5130) required
Resistance to Pressure (FC-5140) needs evaluation for applicability and feasibility
Resistance to Heated Air (FC-5150) and Spot Flame Resistance (FC-5160) not required for filters on temporary systems
Structural Requirements (FC-5170) and Inspection (FC-5200) applicable

## Slide 21: Recommended Test
Resistance to Crushing
  Applies to smaller nipple connected filters installed by hand
  Side load on case simulating the human grip on the case during installation
    Load direction parallel and perpendicular to pleats
  Load based on human pinch and grip strength
  Resistance to airflow and Test Aerosol Particle Penetration performed after crush test

## Slide 22: Article FC-6000 Through FC-9000
Requirements would remain similar but adjusted
Mandatory Appendix FC-I requirements would be the same for filters used in temporary systems

## Slide 23: Conclusion and Recommendation
A new low-flow-rate HEPA filter for use in temporary nuclear systems has been developed and Code requirements have been evaluated
A new Code section is recommended that covers special HEPA filters used for temporary nuclear systems
  Requirements for temporary nuclear systems are different from permanent systems used in nuclear facilities
  New Code section could be expanded to include other temporary systems such as vacuum cleaners