## Slide 1
Fire Detection in Adsorber Beds: Carbon Monoxide Monitoring vs. Thermocouples
NUCON International Inc.
C.B. Summers
J. L. Kovach

## Slide 2: Alarms for Indication of Carbon Bed Fires
Temperature, measured by thermocouple
  High and High-High alarm levels
  Dependent on location of thermocouple in relation to “thermal excursion”
  May indicate only a fully developed fire
Carbon monoxide levels
  More sensitive, only one alarm “level” required
  May be impacted by background CO levels

## Slide 4: Type II Tray Carbon Bed Ignition Studies
Carried out in a wind tunnel built for performing mechanical leak testing of individual Type II filters
Airflow consistent with typical air cleaning system operational conditions (≈ 333 SCFM, ≈ 40 FPM)

## Slide 5: Type II Tray Experimental Design
Thermocouple locations
  Inlet and outlet air temperatures measured in both experiments
  Additional measurement points within the adsorber (Type II tray)nt
Ignition source
  cartridge heater, “hot spot” ignition point

## Slide 6
Type II Tray With Thermocouple and Heater Locations

## Slide 7
Test Wind Tunnel
Thermocouple #12
Thermocouple #10
Thermocouple #11

## Slide 8: Experimental
Type II tray, with thermocouples and cartridge heater in place secured in wind tunnel
System operated for approximately 3 to 5 minutes to determine initial temperature and CO levels
Cartridge heater powered on
Cartridge heater powered off after reaching ignition point
System allowed to run until “obvious” signs of thermal excursion observed
System shut down and monitored until safe

## Slide 13
Chart: Type II Tray Ignition Studies, Temperature Vs. Time

## Slide 14
Chart: Type II Tray Ignition Studies, Temperature Vs Time and CO Concentration

## Slide 15
Chart: Type II Tray Ignition Studies, Temperature Vs Time and CO Concentration
CO | 10 | 19 | 23 | 25 | 50 | 169 | 242 | 493 | 705 | 979 | 1289 | 1484 | 1798 | 2023

## Slide 16
Metal Discoloration

## Slide 17
Metal Discoloration
Cartridge Heater

## Slide 18
Viewed Through Inch Lexan

## Slide 19
Test Wind Tunnel

## Slide 20
Burnt Gasket Material

## Slide 21
Burnt Gasket Material

## Slide 22
Metal Discoloration
Carbon Ash

## Slide 24
T1 = 440 T8 =30
T2 = 32 T10 = 28
T3 = 35

## Slide 25
T1 = 450 T8 =31
T2 = 34 T10 = 30
T3 = 42

## Slide 26
Chart: Type II Tray Ignition Studies, Temperature Vs Time
2.75 inches from ignition point
Tmax = 62° C at ≈ 20 minutes
3.75 inches from ignition point
Tmax = 52° C at ≈ 41 minutes

## Slide 27: Type III Tray Experimental Design
Thermocouple locations
  Inlet and outlet air temperatures measured in both experiments
  Additional measurement points within the adsorber (Type III) down stream of ignition point
  Temperature measurement points within the air channels, out side of the carbon bed
Ignition source
  cartridge heater, “hot spot” ignition point

## Slide 28: Type II Tray Carbon Bed Ignition Studies
Carried out in a wind tunnel built for performing mechanical leak testing of individual Type III and Type IV filters
Airflow consistent with typical air cleaning system operational conditions (≈ 376 SCFM, 0.5 second residence time in a 4 inch deep bed)

## Slide 29
Chart: Temperature vs Time Type III Adsorber

## Slide 30
Chart: [CO] and [CO2] vs Time (seconds)

## Slide 42: Off Gas System Adsorber Bed Ignition Studies
Carried out in 14” diameter vessel
Bed depth ≈ 3 ft
Thermocouples at 3 inch intervals
Air flow ≈ 1.2 CFM (1 ft/min velocity)

## Slide 49
Chart: CO (ppm) Bottom

## Slide 50
Chart: CO (ppm) Top

## Slide 51
Chart: Temperature ° C vs Time

## Slide 52
Chart: Temperature ° C vs Time

## Slide 53
Chart: Carbon Monoxide and Carbon Dioxide (ppm) vs Time

## Slide 54: Conclusions
CO monitoring is effective as a means of fire detection in adsorber beds
Thermocouples used for fire detection in adsorber beds may only be useful if they are located where the fire starts
Thermocouples downstream of an adsorber bank may only indicate a fire once the problem reaches extreme levels
Stopping air flow stops the fire (no more oxygen)
High and High-High temperature alarm points may not be as useful for fire detection in adsorber beds as simple CO monitoring

## Slide 55: Questions?