## Slide 1: HEPA Filter Failure Modes at Elevated Pressure, Temperature and Moisture
International Society for Nuclear Air Treatment Technologies
33rd Nuclear Air Cleaning Conference ● June 22-24, 2014 ● St. Louis, MO
by
Werner Bergman and Gerard Garcia1
Aerosol Science, LLC, Stanwood, WA, wbergman@aerosolscience.com
1Consultant, gerardgarcia.me@gmail.com

## Slide 2
Two HEPA filter failure modes are analyzed
pleat collapse
tears
1
2
w/o
separator
w
separator

## Slide 3
Stress on HEPA filters w/o separators causes pleat collapse
Stress
Stress can reduce stiffness (via heat or wetting) or increase pressure drop (via air flow or loading)

## Slide 4
Camera on exit side of filter shows pleat collapse at increasing DP
4 in. WC
10 in. WC
20 in. WC
32 in WC
Giffin et al, 2012

## Slide 5
Particle deposits that conform to the medium pleats add to the pleat stress

## Slide 6
Embossed medium
HEPA filters w/o separators were used
to study failure modes
Filter pleats
Radial flow HEPA
Giffin et al, 2012

## Slide 7
Giffin et al, 2012
Particle loading is used to stress the HEPA filters
ICET used Al(OH)3 , carbon black and Arizona Road Dust
Pleat
collapse
start
tear
end

## Slide 8
Statistical analysis was used to
Determine DP for pleat collapse
12 tests from Giffin et al, 2012 were grouped by temperature and by the filter design- SC or RC
Each group of data was assumed to be normally distributed
The data groupings were changed to improve outcomes

## Slide 9
The SC and RC filters were analyzed for pleat collapse by particle loading
All particles (CB, Al(OH)3 , and AZ) were included

## Slide 10
The pleat collapse by Al(OH)3 loading was significantly higher than by the other particles

## Slide 11
The higher pleat collapse by Al(OH)3 loading was due to a rigid deposit covering the pleats
Carbon black deposits
The rigid deposit of Al(OH)3 was partially supported by the pleat ends and did not contribute fully to pleat collapse.
Al(OH)3 deposits

## Slide 12
High temperature and increased humidity was used to stress partially loaded HEPA filters
HEPA filters were preloaded to 4 in. WC with Al(OH)3 particles prior to the stress tests
pleat collapse
Giffin et al, 2012

## Slide 13
High temperature at low humidity was used to stress partially loaded HEPA filters
HEPA filters were preloaded to 4 in. WC with Al(OH)3 particles prior to the stress tests
Giffin et al, 2012
pleat collapse

## Slide 14
Analyses at elevated temperature show RC filters have pleat collapse at lower DP than SC filters.

## Slide 15
Summary of ICET tests shows pleat collapse with radial flow HEPA filters depends on two factors
Tightness of filter pack (RC>SC)
Separation inside pleats (SC>RC)
1
2

## Slide 16
Pleat collapse also occurs with axial flow HEPA filters w/o separators (U-pack)
Pleat collapse

## Slide 17
ICET studies show RH < 70% has no effect on filter pleat collapse

## Slide 18
Other studies show clean HEPA filters increase in DP above 95% RH at 122°F
Rudinger et al, 1985

## Slide 19
Other studies show loaded HEPA filters increase in DP above 70% RH at 122°F.
Rudinger et al, 1985
The increased DP due to adsorbed water is likely cause of pleat collapse in the ICET study.

## Slide 20
Theory of pleat collapse is based on plate deflection formula of Young and Budynas (2002)
dP,max = maximum deflection
aP = a constant that depends on the D/W ratio,
W = width between separator peaks or embossments
D = pleat depth
P = applied pressure on the sheet
E = Modulus of elasticity
t = thickness of medium

## Slide 21
When the maximum medium deflection equals half the pleat space, the filter pleat has collapsed
D
1/Ni
1/N0
2X0
2Xi

## Slide 22
Theory was used to determine the effective modulus of elasticity for the radial flow filters
Further improvements are needed to separate filter design elements from the modulus of elasticity.

## Slide 23
At higher stress levels, HEPA filters fail due to medium tears from 2 mechanisms
Bending of the filter pack
1
Pleat rupture
2
Waggoner et al, 2012
Gilbert et al, 1995

## Slide 24
The location of the tears from pack bending is at the highest stress location
Bending of the filter pack w/o screen
Rudinger et al, 1990
Bending of the filter pack near sealant, by ribbon separator
Giffin et al, 2012

## Slide 25
Tears from pleat swelling and rupture occur with weak media, especially when wet
Tears from the AG-1 wet overpressure tests typically occur on the downstream pleats near the bottom sealant filter side by the sealant.
Gilbert et al, 1995
This is the weakest and wettest and location due to water drainage.

## Slide 26
Stress tests showed separatorless HEPA filters were weaker than filters with separators.

## Slide 27
Stress tests showed separatorless HEPA filters were weaker than filters with separators.
There is a common DP failure threshold independent of filter design

## Slide 28
Wetting filters dramatically reduces filter strength.
Tests apply to axial flow, deep pleat, aluminum separators, 1000 cfm,

## Slide 29
AG-1 wet overpressure test approximately follows the statistics of wet filter failures
Typical failure mode is pleat rupture of water weakened medium

## Slide 30
Theory of filter failure by bending of filter pack
Rudinger et al, 1987, 1990

## Slide 31
Theory of filter failure by bending of filter pack
sL = the tensile stress on the filter medium
W = width of the HEPA filter pack
H = height of the HEPA filter pack
D = depth of the medium pleats
t = thickness of HEPA filter medium
p = pitch of the separator corrugation
e = elongation of the medium due to loading in %
DP = pressure drop across the HEPA filter pack
Rudinger et al, 1990)

## Slide 32
Theory of filter pack bending is in approximate agreement with experiments
Rudinger et al, 1990)
DP Calculated, kPa
DP Measured, kPa

## Slide 33
Theory of filter failure by swelling and
rupture of pleats
Rudinger et al, 1990)
The theory does not include the cutting of the medium by the corrugated separators.

## Slide 34
Theory of pleat rupture is in approximate agreement with experiments
Rudinger et al, 1987)
Theory can be improved by include medium cutting by separators

## Slide 35
Conclusions
Statistical analysis was used to understand HEPA filter failure modes of pleat collapse and medium tears.
ICET tests were used to analyze pleat collapse
  Found DP at pleat collapse depends on filter design and temperature for RH < 100%
  Developed theory of pleat collapse based on plate deflection
Medium tears by filter pack bending and pleat rupture were analyzed statistically and the theories reviewed.